GROUND FLOOR PLAN

ADMINISTRATION

Ton = 2.6

Cfm=1285

No of Diffusers = 1

Diffuser Size = 600 x 600 mm

FLXØ550mm Type

OFFICE

Ton = 0.82

Cfm=404

No of Diffusers = 1

Diffuser Size = 300 x 300 mm

FLXØ250mm Type

DIRECTOR / CEO

Ton = 1.42

Cfm=694

No of Diffusers = 2 = 694/2 = 347

Diffuser Size = 300 x 300 mm

FLXØ250mm Type

OFFICE ACCOUNT

Ton = 1.274

Cfm=623

No of Diffusers = 2 = 625/2 = 312

Diffuser Size = 300 x 300 mm

FLXØ250mm Type

OFFICE 01

Ton = 0.3

Cfm=153

No of Diffusers = 1

Diffuser Size = 300 x 300 mm

FLX250mm Type

MEETING

Ton = 2.143

Cfm=1048

No of Diffusers = 3 = 1048/3 = 349

Diffuser Size = 300 x 300 mm

FLXØ250mm Type

RESTAURANT

Ton = 13.6

Cfm=6164

No of Diffusers = 4 = 6164/5 = 1233

Diffuser Size = 600 x 600 mm

FLXØ550mm Type

VIP LOUNGE

Ton = 6.6

Cfm=3356

No of Diffusers = 2 = 3356/2 = 1678

Diffuser Size = 600 x 600 mm

FLXØ550mm Type

VIP CHAMBER 01

Ton = 1.2

Cfm=602

No of Diffusers = 1

Diffuser Size = 450 x 450 mm

FLXØ400mm Type

VIP CHAMBER 02

Ton = 1.7

Cfm=870

No of Diffusers = 1

Diffuser Size = 450 x 450 mm

FLXØ400mm Type

WC NORTH

EX-CFM = 50

No of Disc Valve = 3

Total Passage Area = 100 ft²

No of Disc Valve = 2

Each Disc Valve Cfm = 50

Total EX-CFM = 150+100 = 250

FLXØ150mm Type

WC SOUTH

EX-CFM = 50

No of Disc Valve = 3

Total Passage Area = 119 ft²

No of Disc Valve = 2

Each Disc Valve Cfm = 60

Total EX-CFM = 150+120 = 270

FLXØ150mm Type

MALE WC

EX-CFM = 50

No of Disc Valve = 1

Total Passage Area = 118 ft²

No of Disc Valve = 2

Each Disc Valve Cfm = 60

Total EX-CFM = 50+120 = 170

FLXØ150mm Type

FEMALE WC

EX-CFM = 50

No of Disc Valve = 5

Total Passage Area = 60 ft²

No of Disc Valve = 1

Each Disc Valve Cfm = 60

Total EX-CFM = 250+60 = 310

FLX150mm Type

GRAND TOTAL EX-CFM = 170+310 = 480

KITCHEN HOOD VENTILATION

Kitchen Area = 5.7m x 6.8m

Ex-Cfm = 1200 X 990/1000 = 1188

Ex Duct Size =425W x300H

Total Ex-Cfm = 2 x Ex-Cfm = 2 x 1188 = 2376

Main Duct Size = 550W x 400H

FRESH AIR = 80%

Fresh Air Cfm = 0.8 x 2376 = 1900

FA Duct Size = 450W x 400H

Grill Size = 2000L x 200H x 40T (8-inch Height)

FIRST FLOOR PLAN

MAIN HALL

Ton = 75.5

Cfm=31063

Zone 01 = Main Hall & Excluding Balcony

Zone 02 =Below Balcony Area & Projection Room(278Cfm)

No of Machines = 2 AHU (Each 32.08 Tr, it covers main hall)

= 2 FCU (FCU04A 5.7 Tr & FCU04B 5.8 Tr, it covers below Balcony area & Projection room)

Zone 01

No of Supply Diffuser & Grill = 28 = 30785/28 = 1100

Diffuser Size = 550 x 550mm

Linear Supply Grill Size = 1000L x 250H 50W mm

Linear Return Grill Size = 1500L x 250H 50W mm (18nos of Each Cfm = 1710)

Zone 02

FCU04A = 2200 Cfm

FCU04B = 2487 Cfm

No of Grill = 6 = 4400/6 = 1100

Diffuser Size = 550 x 550mm

FLXØ500mm Type

Total Fresh Air Required = FA-CFM = 1785

Projection Room

Diffuser cfm = 278

Diffuser Size = 250 x250mm

FLX200mm type

HALL 01

Ton = 17.8

Cfm=8787

No of Diffusers = 8 = 8787/8 = 1098

Diffuser Size = 550 x 550mm

FLXØ500mm Type

MEETING HALL & MULTIPURPOSE HALL

Ton = 10.8

Cfm= 4242

No of Diffusers = 4 = 4242/4 = 1081

Diffuser Size = 550 x 550mm

FLXØ500mm Type

Ton = 13.8

Cfm= 5549

No of Diffusers = 6 = 45549/6 = 925

Diffuser Size = 450 x4550mm

FLXØ400mm Type

MALE WC

EX-CFM = 50

No of Disc Valve = 5

Total Passage Area = 288 ft²

No of Disc Valve = 5

Each Disc Valve Cfm = 58

Total EX-CFM = 250+288 = 538

FLXØ150mm Type

FEMALE WC

EX-CFM = 50

No of Disc Valve = 6

Total Passage Area = 125 ft²

No of Disc Valve = 3

Each Disc Valve Cfm = 43

Total EX-CFM = 400+125 = 525

FLX150mm Type

GRAND TOTAL EX-CFM = 538+525 = 1063

MALE WC

EX-CFM = 50

No of Disc Valve = 2

Total Passage Area = 119 ft²

No of Disc Valve = 2

Each Disc Valve Cfm = 60

Total EX-CFM = 100+120= 220

FLXØ150mm Type

FEMALE WC

EX-CFM = 50

No of Disc Valve = 6

Total Passage Area = 174 ft²

No of Disc Valve = 2

Each Disc Valve Cfm = 87

Total EX-CFM = 400+174 = 474

FLX150mm Type

GRAND TOTAL EX-CFM = 219+474 = 693

SECOND FLOOR PLAN

BALCONY

Ton = 30.1

Cfm=10612

No of Diffusers = 8 = 10612/8 = 1327

Diffuser Size = 600 x 600mm

FLXØ550mm Type

MALE WC

EX-CFM = 50

No of Disc Valve = 2

Total Passage Area = 170 ft²

No of Disc Valve = 2

Each Disc Valve Cfm = 85

Total EX-CFM = 100+170= 270

FLXØ150mm Type

FEMALE WC

EX-CFM = 50

No of Disc Valve = 4

Total Passage Area = 125 ft²

No of Disc Valve = 2

Each Disc Valve Cfm = 62.5

Total EX-CFM = 200+125 = 325

FLX150mm Type

GRAND TOTAL EX-CFM = 270+325 = 595